AdiNexus IoT Gateway V2.0 Lite Quick Reference Manual

| Technical Specifications Processor; ESP32-WROOM-32D/U, 240 MHz. Flash / RAM; 16 MB Flash + 320 KB DRAM. Wi-Fi; 802.11 b/g/n, 2.4 GHz. Bluetooth; BLE 4.2 / BT 5.0. Ethernet; 10/100 Mbps, RJ-45. Serial; RS-485. Input Power; 9–36 V DC. Protocols; MQTT, Modbus RTU/TCP, HTTP. Security; TLS 1.2/1.3, WireGuard VPN. OTA Update; Over-the-air via MQTT. Quick Setup 1. Attach Wi-Fi antennas onto SMA ports finger-tight. 2. Connect Ethernet (RJ-45) to router/switch. 3. RS-485 Modbus RTU: wire A(+), B(−) to field device. 4. Modbus TCP: use Ethernet port; assign device IP in dashboard. 5. Connect DC power supply. Both LEDs solid = booting (~30 s). 6. P3 Blue solid = MQTT connected. Confirm in cloud dashboard. Connector Quick Reference POWER INPUT +----------------------------------+ ¦ +9~36V DC GND ¦ <- 2-pin terminal block +------+--------------------+------+ +V GND RS-485 / MODBUS RTU +----------------------------------+ ¦ A(+) B(-) ¦ <- 2-pin terminal block +------+-----------------+---------+ A(+) B(-) [Modbus RTU Device] ETHERNET / MODBUS TCP +----------------------------------+ ¦ RJ-45 LAN Port ¦ <- Ethernet Cable +----------------+-----------------+ ¦ Switch / Router [Modbus TCP Device]. |  | BLE Commissioning — AdiNexusFT App Prerequisites: Bluetooth ON • Location permission granted • Install AdiNexusFT apk from provider Activate BLE mode: Hold gateway button 10–20 s → both LEDs blink in sync. 1; Scan & Connect. a. Open AdiNexusFT, tap Scan. Select AdiNexus-XXXX. b. Tap Connect — BLE GATT pairs automatically (no PIN). 2; Wi-Fi Configuration. a. Tap Wi-Fi tab → select SSID → enter password → tap Apply. 3; MQTT Configuration. a. Tap MQTT tab. Enter Broker URL, Port (1883/8883 TLS), Topic Prefix, Device ID. b. Enter credentials if required → tap Apply. 4; Config Update. a. Tap Config Update. Select/type JSON config → tap Send. b. Device applies config immediately without restart. 5; OTA Firmware Update. a. Tap OTA Update. Select firmware .bin from phone storage. b. Tap Start OTA. Progress bar shown. Device auto-reboots on completion. 6; Device Logs. a. Tap Logs tab to stream real-time logs over BLE. b. Filter by DEBUG/INFO/WARN/ERROR. Tap Export to save to file. 7; Factory Reset via App. a. Tap Factory Reset. Choose Level 1 (config only) or Level 2 (full wipe). b. Confirm prompt — device resets and restarts. 8; Save & Verify. a. Tap Save & Restart. LEDs: both solid (boot) → P3 Blue solid = connected. b. Open cloud dashboard — device appears online within 60 s. |
| --- | --- | --- |

LED Status Indicators   P1 = WiFi LED  |  P2 = Red LED (status/error)  |  P3 = Blue LED (connectivity)  |  ✓ Normal: P3 Blue solid

| Device State | P1 WiFi | P2 Red (status) | P3 Blue (status) | Visual Description |
| --- | --- | --- | --- | --- |
| Boot / Restart | — | Steady | Steady | Both LEDs solid |
| Init Failed | — | Blink 3s | OFF | Red blink only |
| Config from Cloud | — | Steady | Blink 2s | Red solid + Blue blink |
| Config from Binary | — | Blink 2s | Steady | Red blink + Blue solid |
| OTA in Progress | — | Blink 2s | OFF | Red blink only |
| MQTT Connected ✓ | — | OFF | Steady | Blue solid — Normal operation |
| MQTT Disconnected | — | Steady | OFF | Red solid only |
| VPN Mode | — | Alt. 1s | Alt. 1s | Red ↔ Blue alternate (2s cycle) |
| BLE Mode | — | Blink 3s | Blink 3s | Both blink in sync |
| WiFi Connected | Steady | — | — | WiFi LED solid |
| WiFi Disconnected | Blink 2s | — | — | WiFi LED blink |

Button Functions   Press and hold RESET/CONFIG button; release at desired duration to trigger the action.

| Hold Duration | Press Type | Action |
| --- | --- | --- |
| < 50 ms | Noise / bounce | No action — filtered by firmware |
| 50 ms – 5 s | Short press | Save SD card data & restart device |
| 5 s – 10 s | Dead zone | No action — intentionally ignored |
| 10 s – 20 s | Long press | Start BLE commissioning mode |
| 20 s – 30 s | Very long press | Factory Reset Level 1 (config reset, keeps certs) |
| ≥ 30 s | Ultra long press | Factory Reset Level 2 (full wipe & restart) |