## Modbus mapping
16 bit Starting offset: | 400000
32 bit Starting offset: | 420000
Modus mode
Commands | Group | Index | 16bit | 16bit Address | 32bit | 32bit Address | Data type | Unit | Range
Start/Stop Command | 1 | 6 | 106 | 400106 | 212 | 420212 | Real
Pump Status | 6 | 11 | 611 | 400611 | 1222 | 421222 | Real
Actual Speed Feedback | 1 | 2 | 102 | 400102 | 204 | 420204 | Real
Motor Current | 1 | 7 | 107 | 400107 | 214 | 420214 | Real
Fault Code | 4 | 11 | 411 | 400411 | 822 | 420822 | Real
Pump Pressure | 81 | 2 | 8102 | 408102 | 16204 | 436204 | Real |  |  | AQAD203x_en.pdf
Page: 307
[10 empty] | AQAD203x_en.pdf | Page 402
Status code
[10 empty] | value & 0x01 == 1 | Ready
Running
[10 empty] | value & 0x08 == 1 | Tripped/Fault
[10 empty] | AQAD203x_en.pdf | Page 401
Start stop pump
[10 empty] | Start | ?
[10 empty] | Stop | ?

## Faults
Fault Code(Hex) | Fault Code(Decimal) | Fault Name | Description
2281 | 8833 | Current Calibration | Drive current measurement calibration issue
2310 | 8976 | Overcurrent | Motor current exceeded drive limit
2330 | 9008 | Earth Leakage | Ground fault detected
2340 | 9024 | Short Circuit | Output short circuit detected
3130 | 12592 | Input Phase Loss | Missing input supply phase
3181 | 12673 | Wiring / Earth Fault | Incorrect motor or grounding wiring
3210 | 12816 | DC Link Overvoltage | DC bus voltage too high
3220 | 12832 | DC Link Undervoltage | DC bus voltage too low
5080 | 20608 | Cooling Fan Fault | Cooling fan feedback missing
80A0 | 32928 | AI Supervision | Analog input signal supervision fault | This will be mainly because of sensor pressure connected externally to drive. In our case it is pressure transducer
80B0 | 32944 | Signal Supervision 1 | Configured signal monitoring fault | Configured condition from Drive's composer software
80B1 | 32945 | Signal Supervision 2 | Configured signal monitoring fault | Configured condition from Drive's composer software
80B2 | 32946 | Signal Supervision 3 | Configured signal monitoring fault | Configured condition from Drive's composer software
9081 | 36993 | External Fault 1 | External trip from PLC/interlock
9082 | 36994 | External Fault 2 | External trip from PLC/interlock
4310 | 17168 | Excess temperature
50A0 | 20640 | Cooling fan stuck or disconnected.
7121 | 28961 | Motor stall
7310 | 29456 | Overspeed